# Drinking Water Quality and Compliance

for the Hamlet of Dana

c/o Rural Municipality of Bayne No. 371

2022 Annual Notice to Consumers

Introduction

The Water Security Agency (WSA) requires that at least once each year waterworks owners provide notification to consumers of the quality of water produced and supplied as well as information on the performance of the waterworks in submitting samples as required by a Permit to Operate a Waterworks.  The following is a summary of the Hamlet of Dana/Rural Municipality of Bayne No. 371 water quality and sample submission compliance record for the January 1, 2022 to December 31, 2022 time period.  This report was completed on April 25, 2023.  Readers should refer to the Agency’s Municipal Drinking Water Quality Monitoring Guidelines, November 2015, EPB 202 for more information on minimum sample submission requirements and the meaning of type of sample.  Permit requirements for a specific waterworks may require more sampling than outlined in the Agency’s monitoring guidelines.  If consumers need more information on the nature and significance of specific water tests, for example, “what is the significance of Selenium in a water supply”, more detailed information is available from:  http://www.hc-sc.gc.ca/ewh-semt/pubs/water-eau/index_e.html .

## Water Quality Standards

# Bacteriological Quality

Regular Samples	Regular Samples	  # of Positive Regular

Parameter/Location	Limit			Required		Submitted	  Submitted (%)

Total Coliform and	0 Organisms/100 mL	_____12______  ___12_________  ____0%______________

Background Bacteria	Less than 200/100 mL

Water Disinfection –

Chlorine Residual in Distribution System for Test Results Submitted with Bacteriological Samples

Minimum	Total Chlorine	Free Chlorine	# Tests	# Tests	# Adequate

Parameter	Limit	Residual Range	Residual Range	Required	Submitted	Chlorine (%)

Chlorine	0.1 mg/L free OR

Residual	0.5 mg/L total	1.25-1.90	0.03-0.14	    12	     12		100%

Water Disinfection - Free Chlorine Residual for Water Entering Distribution System from Waterworks Records-From Water Treatment Plant Records

Test Level	# Tests                # Tests Not Meeting

Parameter	Limit (mg/L)	Range	Performed          Requirements

Free Chlorine Residual	at least 0.1	0.04-0.14	365	0

A minimum of 0.1 milligrams per litre (mg/L) free chlorine residual is required for water entering the distribution system.  Tests are normally performed on a daily basis by the waterworks operator and are to be recorded in operation records.  This data includes the number of free chlorine residual tests performed, the overall range of free chlorine residual (highest and lowest recorded values) and the number of tests and percentage of results not meeting the minimum requirement of 0.1 mg/L free chlorine residual.

Turbidity – From Water Treatment Plant Records

Parameter	Limit	Test Level	# Tests Not Meeting	Maximum	# Tests           # Tests		# Tests

(NTU) 	Range	Requirements	Turbidity (NTU)	Required        Performed

Turbidity	__1.0_____   .01 – 3.64	_____126___________	___14.53____	 365            365

More information on water quality and sample submission performance may be obtained from:

Rural Municipality of Bayne No. 371

Diana Koenning - Administrator

Box 130 Bruno, SK  S0K 0S0

Phone:  306-369-2511 or fax 306-369-2528

E-mail:  rm371@sasktel.net